Created by Philip Laudicina of Vollmer 05/10/2013

Access Control Maintenance Sheets

You are REQUIRED to fill out each section, 1 per Access Control Panel

Site Name:

Site Address:

Site Contact Name:

Company Performing Maintenance:

Job #:  			Work Order #:

Technician Name:

Maintenance Start Time/Date: 			 Maintenance Completion:

Permit Number (if applicable):

Do you need to return? & Reason?

Did you rent a lift?

If yes please input call off numbers:

Prior Job Comments:

.

AC Panel Location/Name or IP:  ______________________________________________________________________________________

AC Panel Type:  ______________________________________________________________________________________

Communication BUS Type:  ______________________________________________________________________________________

Current Firmware Version Installed: (please indicate if firmware has ROM or Flash RAM):

______________________________________________________________________________________

______________________________________________________________________________________

______________________________________________________________________________________

Updated Firmware Available on Manufacturer's Website?

______________________________________________________________________________________

______________________________________________________________________________________

Firmware Completed?  Y/N? (if no, please explain)

______________________________________________________________________________________

______________________________________________________________________________________

DO NOT upgrade unless you are 100% you are capable of doing this, otherwise just indicate if firmware is available

Onboard Voltage Measurements:

PANEL _____

Main Power Supply Pos + Neg - Measured DC _____________ > (24.6VDC or 13.4VDC Good)

Battery 1 Reading DC No Load __________ > No Load (13.2VDC Good)

Battery 1 Reading DC w /Load  __________ > w /Load (12.9VDC Good)

Battery 2 Reading DC No Load __________ > No Load (13.2VDC Good)

Battery 2 Reading DC w /Load  __________ > w /Load (12.9VDC Good)

Card Reader 1 (Mullion Type) Measured DC ______________ > (12.5 - 13.4VDC Good)

Card Reader 1 (Long Range Type) Measured DC ______________ > 25.0VDC – 30VDC Good)

Card Reader 1 Data – Data +       Measured OHMS 20k_____________ > (1.19  – 1.86 Good)

Lock Output 1 (NO & Common)    Measured OHMS 20k_____________ > (1.25 – 1.30 Normal)

Card Reader 2 (Mullion Type) Measured DC ______________ > (12.5 - 13.4VDC Good)

Card Reader 2 (Long Range Type) Measured DC ______________ > 25.0VDC – 30VDC Good)

Card Reader 2 Data – Data +       Measured OHMS 20k______________ > (1.19 – 1.86 Good)

Lock Output 2 (NO & Common)    Measured OHMS 20k_____________ > (1.25 – 1.30 Normal)

Card Reader 3 (Mullion Type) Measured DC ______________ > (12.5 - 13.4VDC Good)

Card Reader 3 (Long Range Type) Measured DC ______________ > 25.0VDC – 30VDC Good)

Card Reader 3 Data – Data +       Measured OHMS 20k______________ > (1.19 – 1.86 Good)

Lock Output 3 (NO & Common)    Measured OHMS 20k_____________ > (1.25 – 1.30 Normal)

Card Reader 4 (Mullion Type) Measured DC ______________ > (12.5 - 13.4VDC Good)

Card Reader 4 (Long Range Type) Measured DC ______________ > 25.0VDC – 30VDC Good)

Card Reader 4 Data – Data +        Measured OHMS 20k______________ > (1.19 – 1.86 Good)

Lock Output 4 (NO & Common)    Measured OHMS 20k_____________ > (1.25 – 1.30 Normal)

Technician Comments:

Visual Onboard Observations:

Power Supply Module in Cabinet

Is Green AC LED on (left side of Power Supply)?:

Is Red DC LED on (same location)?:

Is Red Batt LED on (same location)?:

Networking

Is the RUN LED status blinking in 1s intervals?:

Do you have a 100M Link Status LED?:

Closing Job Comments or Recommendations: